In buildings required by Code to be fully sprinklered, the Georgia State Fire Marshal’s Office requires automatic fire sprinkler protection to be provided below all drive-thru type canopies per NFPA 13 (1996), Section 4-13.7.1 as automobiles, vans, etc., are subject to driving and/or occasionally standing/parking under the canopy, which introduces combustibles below it. If piping in this areas is subject to freezing temperatures and can not be reliably maintained at or above 40F as required by NFPA 13 (1996), Section 4-14.4.1.1, then a dry pipe type (or anti-freeze type if less than 40 gallon capacity) system is required.