Manual Pull Stations are required by the 2000 IFC, Section 907.4.2 to be mounted 42 to 48-inches above finish floor to the pulling mechanism. Visual notification appliances may be located at least 80-inches from the finish floor of the notification area to the bottom of the strobe lens (or the top of the strobe lens 6-inches below the ceiling – whichever is lower), but top of the strobe lens shall never be higher than 96-inches. The use of ceiling mounted notification appliances are acceptable as complying with the requirements of 120-3-20-.39(3)(f) as an equivalent facilitation per 120-3-20-.04(2) only where wall mounted devices are undesirable due to: obstructions (such as the high shelving) or damage (fork-lift truck high traffic areas); or, where they provide better performance (large open areas where wall mounted devices simply can not provide proper illumination at the area’s center). Ensure strobes are synchronized per GAC requirements. Mounting heights for panels, touchpads, etc. shall comply with 120-3-20-.13 accessibility requirements (max 48-inches forward approach/max 54-inches side approach) to the operating features (door handles, buttons, etc.) of these devices.