Fire Alarm System must comply with GAC (120-3-20), ’97 Life Safety Code (NFPA 101 – 1997), and NFPA 72 (1996) requirements. Visual notification appliances are required in all general usage and common areas as required by 120-3-20-.39 (Georgia Accessibility Code).

120-3-20-08(14) requires visual alarms wherever audible alarms are required and ’97 LSC, Section 7-6.3.5 requires alarm signals throughout the building. Section 7-6.3.4, Exception No.1, permits omitting visual signals for areas not subject to occupancy by persons who are hearing impaired. Also, 120-3-20-.03(3) indicates areas that are used exclusively by employees as a work area (i.e. areas containing only individual work stations such as computer desks, lab tables, etc. and typically not frequented by non-employees such as public/client/patient/detainees) are exempt from the visual notification portion of the accessibility requirements. Other areas used by common or general building occupants (file rooms, copy room, etc.) are required to meet all accessibility requirements including visual notification . 120-3-20-.08(5)(b) indicates rooms typically non-occupiable (locked, not accessible to the common or general building occupants such as janitors room, locked storage rooms, mechanical rooms, electrical rooms, etc., which are not considered general usage or common areas) are not required to meet visual notification accessibility requirements. Also, non-handicap individual cells or non-handicap private/semi-private patient rooms are exempt from visual notification accessibility requirements.