The use of a Fire Pump shall comply with the provisions of NFPA 20 (1999). Any Backflow preventer shall be located a minimum of 10 pipe diameters upstream of the fire pump per NFPA 20 (1999), Section 2-21.3. Fire Department Connections shall not be located upstream of any Fire Pump. The Fire Pump test header shall be sized in accordance with NFPA 20 (1999), Table 2-20 (e.g. 1000gpm pump requires four valves with a minimum 8-inch supply). The fire pump suction supply shall not drop to below 20psi (to prevent introducing contaminants to the potable water supply, pipe cavitations, etc.) as required by 120-3-3 Modification to NFPA 20 which added Section 2-1.1.1. Also, Fire Pump room shall be a minimum 1-hour fire resistance construction per NFPA 20 (1999), Section 2-7.1.1, Exception No.2. Note: All wiring routed through the building for the fire pump shall either be encased in a minimum of 2-inches of concrete cover or protected by a minimum 1-hour electric circuit protective system per 2002 NEC Article 695, Section 695-6(B). Provided the electrical service from is provided by one of the Power Companies of the Southern Companies which is considered a reliable power supply, a secondary power supply to the Fire Pump required by NFPA 20 (1999), Section 6-2.3.1 shall not be required.