  - Provide a site plan indicating locations of Fire Hydrants within 50-feet of the Fire Department Connection (F.D.C.) as required by NFPA 1141 (1990), Section 3-6.2.2. Include the location of Fire Hydrants within 600-feet of all firefighter access points when measured along the normal routes of Fire Department vehicle access as required by the 2000 IFC, Section 508.5.1, Exception #2. NFPA 24 (1995), Section 3-3 requires a Post Indicating Valve (P.I.V.) located a minimum of 40-ft from the building on the water supply serving the Fire Sprinkler Riser. Plan should include any new Fire Hydrant supply pipe routes and sizes, location of valve pits, FDC, etc. per NFPA 24 (1995).

  - Note: Provide a minimum 20-feet of unobstructed roadway clearance for Fire Department Access, including 13-feet 6-inches vertical clearance. Provide marking of Fire Department Access including signage.