A Listed for Fire Protection Service Heat Tracing System (e.g. Tyco Thermal Controls LLC, Thermon Mfg. Co., or EGS Heating Cable Systems – Div. of EGS Electrical Group LLC) is an acceptable method of Freeze Protection. The system shall include the following:

- Heat tracing type/model selected per Manufacturer’s recommendations.

- Insulation per Manufacturer’s Data.

- Connection end pilot light located where it is readily visible upon inspection.

- Thermostats:

  - Ambient Sensing set at 40ºF either directly or through an appropriate contactor.

  - Line Sensing located on opposite end from connection end pilot light.

- Ground fault circuit breaker with a 30mA trip level (such as Square D QO-EPD and QOB-EPP or equivalent) per NEC (NFPA 70, 2000 edition) requirements.

- Monitoring by Fire Alarm System for trouble conditions per NFPA 72 (1996), Section 3-8.6.2.

- Installation:

  - Apply the heater linearly on the pipe after piping has been successfully pressure tested. Secure the heater to piping with cable ties or fiberglass tape.

  - Apply ‘Electric Traced’ signage to the outside of the thermal insulation.

- Tests:

  - After installing and before and after installing the thermal insulation, subject heat to testing using a 2500 VDC megger. Minimum insulation resistance should be 20 megaohms regardless of length.

  - The installer shall test both heating cable bus wires to verify the connection of any splices of tees.