Cooking Operations utilizing Residential Range

  - 120-3-3-.04(70)(a) modifies NFPA 96 (2001), Section 1.1.4, permitting a residential kitchen range to have a Residential Style Hood system equipped with a listed Residential Hood Fire Suppression System provided all the listed conditions are met (e.g. four-burner residential range, etc.). The installing contractor for the hood suppression system should comply with all applicable NFPA 96 provisions that may be feasible. System shall be installed per the manufacturer’s listing requirements. The extinguishing unit shall disconnect electrical power to electric stoves, or shut off the gas supply to gas stoves, with a manual reset. A signed ‘Letter of Intent’ shall be submitted from the owner indicating the hood will be used for ‘food warming and limited cooking only’ as one of the requirements for using this option ~ see item (3) in Section 1.1.4 [note: kitchens serving a large seating area (e.g. with 50 or more occupant load = assembly occupancy), located in a Mercantile Occupancy, or with frying operations, are no longer ‘limited cooking’]. Hood unit shall be ventilated to the exterior of the building per item (4) in Section 1.1.4. Hood to be mounted to provide for thorough cleaning of its surfaces. A minimum Class K Fire Extinguisher should be located within 30-feet of travel distance from the cooking range per NFPA 10.