## Sheet1
H height | W width | L length | Candela Rating | d1 (horiz.) | d2 (linear) | Vertical Angle | 'Quick' % of candela | E - lumens per sq.ft. | Adj. % Table | Adj. E >.03 (ADA)
20 | 20 | 20 | 30 | 14.1421 | 24.4949 | 35.2644 | 0.64736 | 0.032368 | 82 | 0.041
20 | 30 | 30 | 45 | 21.2132 | 29.1548 | 46.6861 | 0.53314 | 0.028225 | 70 | 0.037059
20 | 40 | 40 | 80 | 28.2843 | 34.641 | 54.7356 | 0.45264 | 0.030176 | 45 | 0.03
20 | 50 | 50 | 115 | 35.3553 | 40.6202 | 60.5038 | 0.39496 | 0.027528 | 40 | 0.027879
|  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0!
|  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0!
8 | 20 | 50 | 75 | 26.9258 | 28.0891 | 73.4527 | 0.26547 | 0.025235 | 34 | 0.032319
|  |  |  | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0!
21 | 18 | 60 | 110 | 31.3209 | 37.7094 | 56.159 | 0.43841 | 0.033914 | 45 | 0.03481
Wall mounted appliances to use Table 6-4.4.1.1(a) (NFPA 72) for square areas of coverage. Rectangular shapes use .0375 lumens/sq.ft. per A-6-4.4.1(a) and E=I/d2 where d is horizontal distance (ft) to most remote point of rectangle, I is candela rating, and E is effective lumens density. Ceiling mounted appliances to use above calculation matrix and are limited to a minimum of .03 lumens/sq.ft. per ADA requirements.